FLOAT SWITCH SETTINGS.

TWIN PUMPS.

# Additional notes for on site Electrician.

Create a loop in each of the Float cables using a cable tie, and hang each float switch from the Hook float suspension bracket provided in the Manway opening.

- Float No.1 The lowest float is the common Off Float, set this about 100 - 150mm up from the bottom of the Sump.

- Float No.2 is On / Start for the Duty Pump, Set this say 500mm up from the bottom of the sump.

- Float No.3 is On No.2, Set this a further 150mm up from Float No.2

- Float No.4 This is the highest float, i.e.  the High Level Alarm Float, Set this about 75mm higher than Float No. 3

# As water enters the tank the Off float is tilted nothing happens at this point.

As the water level rises further, the On 1 float is tilted, and the ‘duty’ pump starts. This runs until the Off float drops down. In the unlikely event that the inflow is greater than the pump discharge rate, then On No. 2 float would tilt, and both pumps would run.

There is a stepping relay in the Control Panel. When one particular pump (i.e. the duty pump) completes a pumping cycle. The other pump becomes the duty pump on the next cycle, and so on. Each pump is activated / runs alternatively.

I hope these notes are of some help to you. For more technical electrical details please contact:-Steve Barker or Steve Bourne at Pisces Pumps 01538 361911

Synergy Wastewater Treatment Products Limited.

# E&OE

06.11.15